## DailyOps
Maynardville Wastewater Treatment Plant
Daily Operational Report
2024-04-01
Date |  | Daily Flow |  |  |  | Clarifier1 | Clarifier2 |  | Blowers |  | R.A.S.
| Influent | Effluent | Rainfall | Bleach | NaHSO2 | Sludge | Sludge | Wasting | Blower 1 | Blower 2 | Pump 1 | Pump 2
| Reading | Readiing | Inches | Gal. | Gal. | Depth | Depth | in Hrs. | Hrs Ran | Hrs Ran | Clock Hrs. | Clock Hrs.
1 | 215450 | 228985 | 0 | 21.9 | 7.8 | 3 | 1 | 0 | 12 | 12 | 24 | 0
2 | 230723 | 223391 | 0 | 23.4 | 7.8 | 4 | 1 | 11 | 12 | 12 | 24 | 0
3 | 265446 | 256615 | 0.44 | 21.9 | 7.8 | 3.5 | 1 | 7 | 12 | 12 | 24 | 0
4 | 211075 | 224660 | 0.03 | 34.4 | 7.8 | 3 | 1 | 0 | 12 | 12 | 24 | 0
5 | 215723 | 217327 | 0.04 | 21.1 | 7.8 | 4 | 1 | 0 | 12 | 12 | 24 | 0
6 | 196528 | 214579 | 0 | 34 | 7.8 | 3.8 | 1 | 3 | 12 | 12 | 24 | 0
7 | 194739 | 203049 | 0 | 16.4 | 7.8 | 2.5 | 1 | 0 | 12 | 12 | 24 | 0
8 | 187451 | 214552 | 0 | 16.4 | 7.8 | 3.5 | 1 | 0 | 12 | 12 | 24 | 0
9 | 221868 | 226655 | 0.06 | 12.5 | 7.8 | 3.5 | 1 | 2 | 12 | 12 | 24 | 0
10 | 236339 | 235007 | 0 | 18 | 7.8 | 3.5 | 1 | 7.5 | 12 | 12 | 24 | 0
11 | 430213 | 372435 | 0.45 | 16.4 | 7.8 | 4.5 | 1 | 0 | 12 | 12 | 24 | 0
12 | 376442 | 337888 | 1.14 | 18 | 7.8 | 5.5 | 1 | 0 | 12 | 12 | 24 | 0
13 | 270768 | 256951 | 0.11 | 15.6 | 7.8 | 4 | 1 | 0 | 12 | 12 | 24 | 0
14 | 249345 | 250331 | 0 | 19.5 | 7.8 | 2 | 1 | 0 | 12 | 12 | 24 | 0
15 | 247380 | 254506 | 0 | 14.6 | 7.8 | 3 | 1 | 1 | 12 | 12 | 24 | 0
16 | 185063 | 240082 | 0 | 15.8 | 7.8 | 3 | 1 | 4 | 12 | 12 | 24 | 0
17 | 209862 | 255624 | 0 | 16.8 | 7.8 | 3.5 | 1 | 5 | 12 | 12 | 24 | 0
18 | 218132 | 250178 | 0.02 | 16.4 | 7.8 | 4 | 1 | 5.5 | 12 | 12 | 24 | 0
19 | 219491 | 233036 | 0.15 | 16 | 7.8 | 3.5 | 1 | 0 | 12 | 12 | 24 | 0
20 | 205626 | 218199 | 0 | 17.2 | 7.8 | 4 | 1 | 0 | 12 | 12 | 24 | 0
21 | 199127 | 211624 | 0.14 | 17 | 7.8 | 5 | 1 | 0 | 12 | 12 | 24 | 0
22 | 193608 | 207938 | 0 | 12.3 | 7.8 | 4 | 1 | 0 | 12 | 12 | 24 | 0
23 | 205608 | 101856 | 0 | 14.5 | 7.8 | 3 | 1 | 0 | 12 | 12 | 24 | 0
24 | 207984 | 199932 | 0 | 13.3 | 7.8 | 3 | 1 | 5 | 12 | 12 | 24 | 0
25 | 201666 | 202873 | 0 | 12.1 | 7.8 | 3 | 1 | 5 | 12 | 12 | 24 | 0
26 | 219703 | 206414 | 0.02 | 13.7 | 7.8 | 2.8 | 1 | 5 | 12 | 12 | 24 | 0
27 | 190584 | 188808 | 0.3 | 13.3 | 7.8 | 3 | 1 | 4 | 12 | 12 | 24 | 0
28 | 195032 | 199455 | 0.01 | 12.5 | 7.8 | 2.5 | 1 | 2 | 12 | 12 | 24 | 0
29 | 191410 | 200858 | 0 | 16.4 | 7.8 | 3.1 | 1 | 0 | 12 | 12 | 24 | 0
30 | 215638 | 209542 | 0.16 | 9.4 | 7.8 | 3 | 1 | 7.5 | 12 | 12 | 24 | 0
Total | 6808022 | 6843348 | 3.07 | 520.8 | 234 | 103.7 | 30 | 74.5 | 360 | 360 | 720 | 0

## State1
Maynardville Wastewater Treatment Plant M.O.R. / APRIL 2024 | [30 empty] | MGD FLOWS |  | LBS CALCULATIONS
|  | PLANT FLOWS |  |  | TEMP. |  | 5 DAY C. B.O.D. |  |  |  | SUSPENDED SOLIDS |  |  |  | SETTLED SOLIDS |  | DISSOLVED OXYGEN |  | pH |  | AMMONIA NITROGEN | [6 empty] | CHEMICAL USAGE |  |  | INF | EFF | 5 DAY B.O.D. |  | SUSPENDED SOLIDS |  | AMMONIA NITROGEN
D | DAILY | INFLUENT | EFFLUENT | HOURS | RAW | FINAL | [18 empty] | EFFLUENT | EFFLUENT | EFFLUENT | Gal. | Gal. |  | DAILY | DAILY | [6 empty] | Plant Effeciencies
A | RAIN | FLOW | FLOW | PLANT | WASTE | EFF | PLANT | FINAL | FINAL | FINAL | PLANT | FINAL | FINAL | FINAL | PLANT | FINAL | PLANT | FINAL | PLANT | FINAL | PLANT | FINAL | FINAL | FINAL | E |  | CL-2 | of | of |  | FLOW | FLOW | PLANT | FINAL | PLANT | FINAL | PLANT | FINAL
T | FALL |  |  | BY | TEMP. | TEMP | INF. | EFF. | EFF. | EFF. | INF. | EFF. | EFF. | EFF. | INF. | EFF. | INF. | EFF. | INF. | EFF. | INF. | EFF. | EFF. | EFF. | COLI |  | RES. | Bleach | NaHSO2 |  | RATE | RATE | INF. | EFF. | INF. | EFF. | INF. | EFF. | 5 DAY B.O.D. | SUSPENDED SOLIDS | AMMONIA NITROGEN
E | INCHES | MGD | MGD | PASSED | (CEL) | CEL | MG/L | MG/L | LBS | % Removal | MG/L | MG/L | LBS | % Removal | ML/L | ML/L | MG/L | MG/L | MG/L | MG/L | MG/L | MG/L | LBS | % Removal | #/100 ML |  | MG/L | USED | USED |  | MGD | MGD | LBS | LBS | LBS | LBS | LBS | LBS | % Removal | % Removal | % Removal
1 | 0 | 0.215 | 0.228 | 0 | 14.8 | 16.4 | 271.3 | 4.5 | 8.55 | 98.3% | 136 | 5.2 | 9.9 | 96.2% | 27 | 0 | 2.6 | 6.6 | 7.9 | 7.5 | 35.4 | 0.5 | 0.95 | 98.6% | 1 |  | 0.02 | 21.9 | 7.8 |  | 0.215 | 0.228 | 486.5 | 8.6 | 243.9 | 9.9 | 63.5 | 1 | 98.3% | 96.18% | 98.59%
2 | 0 | 0.23 | 0.223 | 0 | 14.8 | 17 | 242.3 | 4.8 | 8.9 | 98% | 220 | 4 | 7.4 | 98.2% | 19 | 0 | 3.2 | 6.2 | 7.8 | 7.5 | 27.9 | 0.3 | 0.6 | 98.9% | 1 |  | 0.02 | 23.4 | 7.8 |  | 0.23 | 0.233 | 464.8 | 8.9 | 422 | 7.4 | 53.5 | 0.6 | 98% | 98.18% | 98.92%
3 | 0.44 | 0.265 | 0.256 | 0 | 14.8 | 16.6 | 146.4 | 6.5 | 13.9 | 95.6% | 100 | 2.4 | 5.1 | 97.6% | 37 | 0 | 3.8 | 6.4 | 7.8 | 7.6 | 24.1 | 1 | 2.13 | 98.85% | 1 |  | 0.01 | 21.1 | 7.8 |  | 0.265 | 0.256 | 323.6 | 13.9 | 221 | 5.1 | 53.3 | 2.1 | 95.6% | 97.6% | 95.85%
4 | 0.03 | 0.211 | 0.224 | HOURS PLANT BY: 0; RAW WASTE TEMP.: 14.3; FINAL EFF TEMP: 15.4; FINAL PLANT INF.: 19; FINAL FINAL EFF.: 0; FINAL PLANT INF.: 3; FINAL FINAL EFF.: 6.5; FINAL PLANT INF.: 7.8; FINAL FINAL EFF.: 7.5 |  | 0.02 | 34.3 | 7.8 |  | 0.211 | 0.224
5 | 0.04 | 0.215 | 0.217 | HOURS PLANT BY: 0; RAW WASTE TEMP.: 14.3; FINAL EFF TEMP: 14.8; FINAL PLANT INF.: 18; FINAL FINAL EFF.: 0; FINAL PLANT INF.: 2; FINAL FINAL EFF.: 6.8; FINAL PLANT INF.: 7.9; FINAL FINAL EFF.: 7.5 |  | 0.02 | 21.1 | 7.8 |  | 0.215 | 0.217
6 | 0 | 0.196 | 0.214 | HOURS PLANT BY: 0 |  |  | 17.2 | 7.8 |  | 0.196 | 0.214
7 | 0 | 0.194 | 0.203 | 0 |  |  | 343.9 | 5.15 | 8.8 | 98.5% | 248 | 6.4 | 10.8 | 97.4% | 25 | 0 |  |  |  |  | 26.9 | 0.1 | 0.169 | 99.6% | 1 |  |  | 16.4 | 7.8 |  | 0.194 | 0.203 | 556.4 | 8.8 | 401.3 | 10.8 | 43.5 | 0.2 | 98.5% | 97.42% | 99.63%
8 | 0 | 0.187 | 0.214 | 0 | 14.4 | 15.6 | 259.3 | 5.9 | 10.5 | 97.7% | 212 | 6 | 10.7 | 97.2% | 20 | 0 | 2.9 | 6.4 | 7.8 | 7.5 | 25.2 | 0.2 | 0.4 | 99.2% | 1 |  | 0.02 | 16.4 | 7.8 |  | 0.187 | 0.214 | 404.4 | 10.5 | 330.6 | 10.7 | 39.3 | 0.4 | 97.72% | 97.17% | 99.21%
9 | 0.06 | 0.221 | 0.226 | 0 | 15.4 | 15.9 | 234.6 | 6.1 | 11.5 | 97.4% | 1060 | 4.4 | 8.3 | 99.6% | 25 | 0 | 1.4 | 6.8 | 7.75 | 7.5 |  |  |  |  | 4.1 |  | 0 | 12.5 | 7.8 |  | 0.221 | 0.226 | 432.4 | 11.5 | 1953.7 | 8.3 |  |  | 97.4% | 99.58%
10 | 0 | 0.236 | 0.235 | HOURS PLANT BY: 0; RAW WASTE TEMP.: 15.8; FINAL EFF TEMP: 16.4; FINAL PLANT INF.: 25; FINAL FINAL EFF.: 0; FINAL PLANT INF.: 2.5; FINAL FINAL EFF.: 6.65; FINAL PLANT INF.: 7.9; FINAL FINAL EFF.: 7.55; FINAL PLANT INF.: 34; FINAL FINAL EFF.: 0.7; FINAL FINAL EFF.: 1.4; FINAL FINAL EFF.: 97.94% |  | 0 | 18 | 7.8 |  | 0.236 | 0.235 |  |  |  |  | 66.9 | 1.4 |  |  | 97.94%
11 | 0.45 | 0.43 | 0.372 | HOURS PLANT BY: 0; RAW WASTE TEMP.: 15.1; FINAL EFF TEMP: 16.6; FINAL PLANT INF.: 15; FINAL FINAL EFF.: 0; FINAL PLANT INF.: 2; FINAL FINAL EFF.: 6.4; FINAL PLANT INF.: 7.9; FINAL FINAL EFF.: 7.6 |  | 0.01 | 16.4 | 7.8 |  | 0.43 | 0.372
12 | 1.14 | 0.376 | 0.337 | HOURS PLANT BY: 0; RAW WASTE TEMP.: 14.5; FINAL EFF TEMP: 15.9; FINAL PLANT INF.: 5; FINAL FINAL EFF.: 6.5; FINAL PLANT INF.: 7.85; FINAL FINAL EFF.: 7.6 |  | 0 | 18 | 7.8 |  | 0.376 | 0.337
13 | 0.11 | 0.27 | 0.256 | HOURS PLANT BY: 0 |  |  | 15.6 | 7.8 |  | 0.27 | 0.256
14 | 0 | 0.249 | 0.25 | HOURS PLANT BY: 0; FINAL PLANT INF.: 21; FINAL FINAL EFF.: 0; EFFLUENT E COLI: 1 |  |  | 19.5 | 7.8 |  | 0.249 | 0.25
15 | 0 | 0.247 | 0.254 | 0 | 15.7 | 16.3 | 229.6 | 4.4 | 9.3208 | 98.08% | 276 | 10 | 21.1836 | 96.38% | 15 | 0 | 2.4 | 6.6 | 7.7 | 7.6 | 34.1 | 1.5 | 3.1775 | 95.6% |  |  | 0.02 | 14.6 | 7.8 |  | 0.247 | 0.254 | 472.9714 | 9.3208 | 568.5545 | 21.1836 | 70.2453 | 3.1775 | 98.08% | 96.38% | 95.6%
16 | 0 | 0.185 | 0.24 | 0 | 15.4 | 16.9 | 243.5 | 6.6 | 13.2106 | 97.29% | 236 | 5.6 | 11.209 | 97.63% | 16 | 0 | 2.9 | 6.5 | 7.9 | 7.5 | 30.5 | 2 | 4.0032 | 93.44% | 2 |  | 0.01 | 15.8 | 7.8 |  | 0.185 | 0.24 | 375.6961 | 13.2106 | 364.1244 | 11.209 | 47.0585 | 4.0032 | 97.29% | 97.63% | 93.44%
17 | 0 | 0.209 | 0.255 | 0 | 15.9 | 17.1 | 295.02 | 4.9 | 10.4208 | 98.34% | 268 | 1.2 | 2.552 | 99.55% | 27 | 0 | 2.5 | 6.6 | 7.8 | 7.5 | 35 | 3.2 | 6.8054 | 90.86% | 1 |  | 0.01 | 16.8 | 7.8 |  | 0.209 | 0.255 | 514.2376 | 10.4208 | 467.1401 | 2.552 | 61.0071 | 6.8054 | 98.34% | 99.55% | 90.86%
18 | 0.02 | 0.218 | 0.25 | HOURS PLANT BY: 0; RAW WASTE TEMP.: 16.4; FINAL EFF TEMP: 17.5; FINAL PLANT INF.: 29; FINAL FINAL EFF.: 0; FINAL PLANT INF.: 2.6; FINAL FINAL EFF.: 6.6; FINAL PLANT INF.: 7.8; FINAL FINAL EFF.: 7.5; EFFLUENT E COLI: 1 |  | 0.02 | 16.4 | 7.8 |  | 0.218 | 0.25
19 | 0.15 | 0.219 | 0.233 | HOURS PLANT BY: 0; RAW WASTE TEMP.: 16.2; FINAL EFF TEMP: 17.7; FINAL PLANT INF.: 1.1; FINAL FINAL EFF.: 6.4; FINAL PLANT INF.: 7.9; FINAL FINAL EFF.: 7.5 |  | 0 | 16 | 7.8 |  | 0.219 | 0.233
20 | 0 | 0.205 | 0.218 | HOURS PLANT BY: 0 |  |  | 17.2 | 7.8 |  | 0.205 | 0.218
21 | 0.14 | 0.199 | 0.211 | 0 |  |  | 275.04 | 4.4 | 7.7429 | 98.4% | 252 | 4.4 | 7.7429 | 98.25% | 21 | 0 |  |  |  |  | 33.3 | 0.96 | 1.6894 | 97.12% | 6.3 |  |  | 17 | 7.8 |  | 0.199 | 0.211 | 456.4729 | 7.7429 | 418.2343 | 7.7429 | 55.2667 | 1.6894 | 98.4% | 98.25% | 97.12%
22 | 0 | 0.193 | 0.207 | 0 | 15.2 | 16 | 332.9 | 5 | 8.6319 | 98.5% | 428 | 3.6 | 6.215 | 99.16% | 24 | 0 | 1.4 | 6.6 | 8.1 | 7.55 | 36.9 | 1 | 1.7264 | 97.29% | 1 |  | 0.02 | 12.3 | 7.8 |  | 0.193 | 0.207 | 535.8425 | 8.6319 | 688.9174 | 6.215 | 59.395 | 1.7264 | 98.5% | 99.16% | 97.29%
23 | 0 | 0.205 | 0.101 | 0 | 15.1 | 15.8 | 347.6 | 6.5 | 5.4752 | 98.13% | 268 | 1.6 | 1.3477 | 99.4% | 20 | 0 | 2.1 | 6.6 | 7.8 | 7.55 | 30.6 | 1.5 | 1.2635 | 95.1% | 1 |  | 0 | 14.5 | 7.8 |  | 0.205 | 0.101 | 594.2917 | 5.4752 | 458.1996 | 1.3477 | 52.3168 | 1.2635 | 98.13% | 99.4% | 95.1%
24 | 0 | 0.207 | 0.199 | HOURS PLANT BY: 0; RAW WASTE TEMP.: 17.6; FINAL EFF TEMP: 17.9; FINAL PLANT INF.: 26; FINAL FINAL EFF.: 0; FINAL PLANT INF.: 1.5; FINAL FINAL EFF.: 6.2; FINAL PLANT INF.: 7.6; FINAL FINAL EFF.: 7.5 |  | 0.02 | 13.3 | 7.8 |  | 0.207 | 0.199
25 | 0 | 0.201 | 0.202 | HOURS PLANT BY: 0; RAW WASTE TEMP.: 15.5; FINAL EFF TEMP: 16.7; FINAL PLANT INF.: 28; FINAL FINAL EFF.: 0; FINAL PLANT INF.: 2.1; FINAL FINAL EFF.: 6.8; FINAL PLANT INF.: 7.8; FINAL FINAL EFF.: 7.6 |  | 0.01 | 12.1 | 7.8 |  | 0.201 | 0.202
26 | 0.02 | 0.219 | 0.206 | HOURS PLANT BY: 0; RAW WASTE TEMP.: 16.1; FINAL EFF TEMP: 17.2; FINAL PLANT INF.: 1.3; FINAL FINAL EFF.: 6.6; FINAL PLANT INF.: 7.9; FINAL FINAL EFF.: 7.5 |  | 0.02 | 13.7 | 7.8 |  | 0.219 | 0.206
27 | 0.3 | 0.19 | 0.188 | HOURS PLANT BY: 0 |  |  | 13.3 | 7.8 |  | 0.19 | 0.188
28 | 0.01 | 0.195 | 0.199 | 0 |  |  | 356.5 | 3.6 | 5.9748 | 98.99% | 256 | 5.6 | 9.2941 | 97.81% | 24 | 0 |  |  |  |  | 46.2 | 1 | 1.6597 | 97.84% | 1 |  |  | 12.5 | 7.8 |  | 0.195 | 0.199 | 579.7759 | 5.9748 | 416.3328 | 9.2941 | 75.1351 | 1.6597 | 98.99% | 97.81% | 97.84%
29 | 0 | 0.191 | 0.2 | 0 | 16.4 | 18.1 | 277.3 | 2.9 | 4.8372 | 98.95% | 304 | 7.2 | 12.0096 | 97.63% | 25 | 0 | 1.8 | 6.6 | 7.7 | 7.6 | 43.5 | 1.3 | 2.1684 | 97.01% | 1 |  | 0 | 16.4 | 7.8 |  | 0.191 | 0.2 | 441.7223 | 4.8372 | 484.2538 | 12.0096 | 69.2929 | 2.1684 | 98.95% | 97.63% | 97.01%
30 | 0.16 | 0.215 | 0.209 | 0 | 18.7 | 18.6 | 321.1 | 1.5 | 2.6146 | 99.53% | 304 | 3.2 | 5.5778 | 98.95% | 20 | 0 | 0.1 | 6.4 | 7.7 | 7.7 | 33.1 | 0.724 | 1.262 | 97.81% | 1 |  | 0.01 | 9.4 | 7.8 |  | 0.215 | 0.209 | 575.7644 | 2.6146 | 545.1024 | 5.5778 | 59.3516 | 1.262 | 99.53% | 98.95% | 97.81%
TOT | 3.07 | 6.793 | 6.827 | 0 | 342.4 | 366.4 | 4176.36 | 72.75 | 130.3787 | 1472% | 4568 | 70.8 | 129.3317 | 1471% | 526 | 0 | 50.2 | 143.75 | 172.1 | 165.95 | 496.7 | 15.984 | 29.4045 | 1455% | 25.4 |  | 0.26 | 520.8 | 234 | Total | 6.793 | 6.837 | 7214.8748 | 130.4287 | 7983.3592 | 129.3317 | 869.0689 | 29.4555 | 1472% | 1471% | 1455%
AVG. | 0.10233 | 0.22643 | 0.22757 | 0 | 15.5636 | 16.6545 | 278.424 | 4.85 | 8.6919 | 98.11% | 304.5333 | 4.72 | 8.6221 | 98.06% | 22.8696 | 0 | 2.2818 | 6.5341 | 7.8227 | 7.5432 | 33.1133 | 1.0656 | 1.9603 | 97.01% | 1.5875 |  | 0.011818 | 17.36 | 7.8 | Avg | 0.22643 | 0.2279 | 480.5982 | 8.7021 | 552.8185 | 8.5308 | 57.5406 | 2.0325 | 98.12% | 98.06% | 96.81%
MAX. | 1.14 | 0.43 | 0.372 | 0 | 18.7 | 18.6 | 356.5 | 6.6 | 13.9 | 99.53% | 1060 | 10 | 21.1836 | 99.6% | 37 | 0 | 5 | 6.8 | 8.1 | 7.7 | 46.2 | 3.2 | 6.8054 | 99.6% | 6.3 |  | 0.02 | 34.3 | 7.8 | Max | 0.43 | 0.372 | 594.2917 | 13.9 | 1953.7 | 21.1836 | 75.1351 | 6.8054 | 99.53% | 99.58% | 99.63%
MIN. | 0 | 0.185 | 0.101 | 0 | 14.3 | 14.8 | 146.4 | 1.5 | 2.6146 | 95.6% | 100 | 1.2 | 1.3477 | 96.2% | 15 | 0 | 0.1 | 6.2 | 7.6 | 7.5 | 24.1 | 0.1 | 0.169 | 90.86% | 1 |  | 0 | 9.4 | 7.8 | Min | 0.185 | 0.101 | 323.6 | 2.6146 | 221 | 1.3477 | 39.3 | 0.2 | 95.6% | 96.18% | 90.86%
Signature: Michael Payne Cert: # On File

## Aeration
2024-04-01 | [19 empty] | Calculation of
| AERATION BASIN # 1 | [9 empty] | AERATION BASIN # 2
D
A |  | SETTABLE | SETTABLE | SLUDGE | TOTAL | VOLATILE | [5 empty] | SETTABLE | SLUDGE | TOTAL | VOLATILE
T | MLSS | SOLIDS | SOLIDS | VOLUME | SOLDS | SOLDS | D.O. | pH | TEMP. | F/M | MLSS | SOLIDS | VOLUME | SOLDS | SOLDS | D.O. | pH | TEMP. | F/M
E | MG/L | ML/L | ML/L | INDEX | % | % | MG/L | UNITS | CEL. | RATIO | MG/L | ML/L | INDEX | % | % | MG/L | UNITS | CEL. | RATIO | AERATION LBS | AERATION MLVSS LBS | AerMLVSS
E: 1; ML/L: 900; MG/L: 0.2; UNITS: 7.4; CEL.: 15.4; ML/L: 890; MG/L: 1.5; UNITS: 7.4; CEL.: 13.4 | 0 |  | #REF!
E: 2; MG/L: 3858; ML/L: 895; MG/L: 0.3; UNITS: 7.3; CEL.: 16.1; MG/L: 3947; ML/L: 930; MG/L: 1.2; UNITS: 7.3; CEL.: 14 | 16087.86 |  | #REF!
E: 3; MG/L: 3540; ML/L: 890; MG/L: 0.2; UNITS: 7.3; CEL.: 15.9; MG/L: 3722; ML/L: 900; MG/L: 1.2; UNITS: 7.3; CEL.: 14 | 14761.8 |  | #REF!
E: 4; MG/L: 3514; ML/L: 850; MG/L: 0.6; UNITS: 7.35; CEL.: 15.4; MG/L: 3428; ML/L: 870; MG/L: 1.6; UNITS: 7.35; CEL.: 13.4 | 14653.38 |  | #REF!
E: 5; ML/L: 900; MG/L: 0.2; UNITS: 7.36; CEL.: 14.7; ML/L: 930; MG/L: 1.9; UNITS: 7.36; CEL.: 12.7 | 0 |  | #REF!
E: 6; ML/L: 900; MG/L: 0.8; CEL.: 14.4; ML/L: 880; MG/L: 1.7; CEL.: 12.4 | 0 |  | #REF!
E: 7; ML/L: 870; MG/L: 0.5; CEL.: 14.5; ML/L: 890; MG/L: 1.5; CEL.: 12.5 | 0 |  | #REF!
E: 8; MG/L: 3934; ML/L: 950; MG/L: 0.2; UNITS: 7.3; CEL.: 15.1; MG/L: 4028; ML/L: 930; MG/L: 1; UNITS: 7.3; CEL.: 13 | 16404.78 |  | #REF!
E: 9; MG/L: 4192; ML/L: 910; MG/L: 0.2; UNITS: 7.3; CEL.: 15.4; MG/L: 4468; ML/L: 930; MG/L: 1.2; UNITS: 7.3; CEL.: 13.4 | 17480.64 |  | #REF!
E: 10; MG/L: 4160; ML/L: 900; MG/L: 0.2; UNITS: 7.2; CEL.: 15.6; MG/L: 4522; ML/L: 920; MG/L: 1.5; UNITS: 7.2; CEL.: 13.6 | 17347.2 |  | #REF!
E: 11; ML/L: 920; MG/L: 0.2; UNITS: 7.35; CEL.: 16.1; ML/L: 930; MG/L: 0.8; UNITS: 7.35; CEL.: 14 | 0 |  | #REF!
E: 12; ML/L: 850; MG/L: 0.2; UNITS: 7.3; CEL.: 15.2; ML/L: 870; MG/L: 1.6; UNITS: 7.3; CEL.: 13.4 | 0 |  | #REF!
E: 13; ML/L: 850; MG/L: 1.4; CEL.: 14.8; ML/L: 870; MG/L: 1.6; CEL.: 12.8 | 0 |  | #REF!
E: 14; ML/L: 790; MG/L: 0.2; CEL.: 15; ML/L: 830; MG/L: 1.2; CEL.: 13 | 0 |  | #REF!
E: 15; ML/L: 810; MG/L: 0.3; UNITS: 7.35; CEL.: 15.6; ML/L: 860; MG/L: 2; UNITS: 7.35; CEL.: 13.7 | 0 |  | #REF!
16 | 3380 |  | 820 | 242.6036 |  |  | 0.2 | 7.4 | 16.1 |  | 3782 | 870 | 230.037 |  |  | 1.6 | 7.38 | 14.2 |  | 14094.6 |  | #REF!
17 | 3716 |  | 840 | 226.0495 |  |  | 0.2 | 7.3 | 16.6 |  | 4098 | 850 | 207.4183 |  |  | 1.4 | 7.3 | 14.5 |  | 15495.72 |  | #REF!
18 | 3874 |  | 900 | 232.318 |  |  | 0.2 | 7.3 | 16.5 |  | 4152 | 870 | 209.5376 |  |  | 1.5 | 7.3 | 14.5 |  | 16154.58 |  | #REF!
E: 19; ML/L: 910; MG/L: 0.2; UNITS: 7.3; CEL.: 17.1; ML/L: 890; MG/L: 1; UNITS: 7.3; CEL.: 15.1 | 0 |  | #REF!
E: 20; ML/L: 880; MG/L: 0.2; CEL.: 17.3; ML/L: 900; MG/L: 1.5; CEL.: 15.2 | 0 |  | #REF!
E: 21; ML/L: 900; MG/L: 0.2; CEL.: 16.9; ML/L: 900; MG/L: 1.4; CEL.: 14.8 | 0 |  | #REF!
22 | 4806 |  | 930 | 193.5081 |  |  | 0.2 | 7.4 | 16.1 |  | 4882 | 940 | 192.544 |  |  | 1.4 | 7.4 | 14.1 |  | 20041.02 |  | #REF!
23 | 4792 |  | 980 | 204.5075 |  |  | 0.2 | 7.4 | 16.1 |  | 5272 | 960 | 182.0941 |  |  | 1.3 | 7.4 | 14.1 |  | 19982.64 |  | #REF!
24 | 3612 |  | 880 | 243.6323 |  |  | 0.2 | 7.3 | 16.6 |  | 3434 | 820 | 238.7886 |  |  | 1 | 7.3 | 14.5 |  | 15062.04 |  | #REF!
E: 25; ML/L: 800; MG/L: 0.2; UNITS: 7.4; CEL.: 16.6; ML/L: 850; MG/L: 1.5; UNITS: 7.4; CEL.: 14.5 | 0 |  | #REF!
E: 26; ML/L: 850; MG/L: 0.2; UNITS: 7.4; CEL.: 16.9; ML/L: 830; MG/L: 1.3; UNITS: 7.4; CEL.: 14.9 | 0 |  | #REF!
E: 27; ML/L: 800; MG/L: 0.2; CEL.: 16.8; ML/L: 810; MG/L: 1.2; CEL.: 14.7 | 0 |  | #REF!
E: 28; ML/L: 790; MG/L: 0.2; CEL.: 17; ML/L: 810; MG/L: 1.2; CEL.: 15 | 0 |  | #REF!
29 | 3562 |  | 830 | 233.0152 |  |  | 0.2 | 7.4 | 17.4 |  | 3860 | 880 | 227.9793 |  |  | 1.3 | 7.4 | 15.5 |  | 14853.54 |  | #REF!
30 | 3476 |  | 880 | 253.1646 |  |  | 0.3 | 7.3 | 18 |  | 3676 | 860 | 233.9499 |  |  | 1.4 | 7.3 | 15.9 |  | 14494.92 |  | #REF!
[20 empty] | 0 |  | #REF!
TOT | 54416 | 0 | 26175 | 1828.7988 |  |  | 8.8 | 161.41 | 481.2 |  | 57271 | 26470 | 1722.3488 |  |  | 41.5 | 161.39 | 420.8 |  | 226914.72 | 0
AVG. | 3886.8571 | #DIV/0! | 872.5 | 228.5998 |  |  | 0.29333 | 7.3368 | 16.04 |  | 4090.7857 | 882.3333 | 215.2936 |  |  | 1.3833 | 7.3359 | 14.0267 |  | 7319.8297 | #DIV/0!
MAX. | 4806 | 0 | 980 | 253.1646 |  |  | 1.4 | 7.4 | 18 |  | 5272 | 960 | 238.7886 |  |  | 2 | 7.4 | 15.9 |  | 20041.02 | 0
MIN. | 3380 | 0 | 790 | 193.5081 |  |  | 0.2 | 7.2 | 14.4 |  | 3428 | 810 | 182.0941 |  |  | 0.8 | 7.2 | 12.4 |  | 0 | 0

## Stream Data
Maynardville Wastewater Treatment Plant M.O.R. / APRIL 2024
RECEIVING STREAM
D | BOD-5 |  | SUSPENDED SOLIDS |  | SETTABLE SOLIDS |  | DISSOLVED OXYGEN |  | pH UNITS |  | TEMP |  | ECOLI |  | AMMONIA NITROGEN
A
T
E | ABOVE | BELOW | ABOVE | BELOW | ABOVE | BELOW | ABOVE | BELOW | ABOVE | BELOW | ABOVE | BELOW | ABOVE | BELOW | ABOVE | BELOW
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18 | 1.6 | 1.1 | 2 | 1.6 | 0 | 0 | 9.9 | 9.3 | 8.4 | 8.2 | 16.1 | 16.5 | 159.7 | 61.7 | <0.100 | 0.36
19
20
21
22
23
24
25
26
27
28
29
30
TOT | 1.6 | 1.1 | 2 | 1.6 | 0 | 0 | 9.9 | 9.3 | 8.4 | 8.2 | 16.1 | 16.5 | 159.7 | 61.7 | <0.100 | 0.36
AVG. | 1.6 | 1.1 | 2 | 1.6 | 0 | 0 | 9.9 | 9.3 | 8.4 | 8.2 | 16.1 | 16.5 | 159.7 | 61.7 | <0.100 | 0.36
MAX. | 1.6 | 1.1 | 2 | 1.6 | 0 | 0 | 9.9 | 9.3 | 8.4 | 8.2 | 16.1 | 16.5 | 159.7 | 61.7 | <0.100 | 0.36
MIN. | 1.6 | 1.1 | 2 | 1.6 | 0 | 0 | 9.9 | 9.3 | 8.4 | 8.2 | 16.1 | 16.5 | 159.7 | 61.7 | <0.100 | 0.36

## DMR
PERMITTEE NAME/ADDRESS (Include |  |  |  | NATIONAL POLLUTANT DISCHARGE ELIMINATION SYSTEM (NPDES)
Facility Name/Location if different) |  |  |  |  | DISCHARGE MONITORING REPORT (DMR) |  |  |  |  | Form Approved
Name | Maynardville WWTP |  |  | (2-16) |  |  | (17-19) | Minor |  | OMB | No. | 2040-004
Address | P.O. Box 217 |  |  | TN0022870 |  |  | 001 G | Design Capacity of .6 MGD
| Maynardville, TN 37807 |  |  | PERMIT NUMBER |  |  | DISCHARGE NUMBER | (SUBR 03)
[8 empty] | F - Final | BJB
Facility | Maynardville STP |  |  |  | MONITORING PERIOD |  |  | Design Capacity of .6 MGD
Location | Maynardville, TN 37807 |  |  | FROM YEAR MO | DAY | TO YEAR MO | DAY
|  |  |  | 0 | 1 | 0 | 0 | *** No Discharge |  | ***
Michael Payne-Utility Director |  |  |  | (20-21) (22-23) | (24-25) | (26-27) (28-29) | (30-31) | Note: Read Instructions Before Completing this form.
|  |  | (3 Card Only) QUANTITY OR LOADING |  |  | (4 Card Only) | QUALITY OR CONCENTRATION |  |  | NO. | FREQUENCY | SAMPLE
PARAMETER |  |  | (46-53) | (54-61) |  | (38-45) | (46-53) | (54-61) |  | EX | OF ANALYSIS | TYPE
| (32-37) |  | AVERAGE | MAXIMUM | UNITS | MINIMUM | AVERAGE | MAXIMUM | UNITS | (62-63) | (64-68) | (69-70)
Oxygen, Dissolved (DO) |  | SAMPLE | ***** | ***** | ***** | 6.2 | ***** | ***** | (19) | 0 | 5/7 | Grab
00300 | 1 0 0 | MEASUREMENT | [6 empty] | mg/l
Effluent Gross Value |  | PERMIT | ***** | ***** | ***** | 5 | ***** | ***** |  |  | Weekdays | Grab
|  | REQUIREMENT |  |  |  | Inst Min.
pH |  | SAMPLE | ***** | ***** | ***** | 7.5 | ***** | 7.7 | (12) | 0 | 5/7 | Grab
00400 | 1 0 0 | MEASUREMENT | [6 empty] | SU
Effluent Gross Value |  | PERMIT | ***** | ***** | ***** | 6 | ***** | 9 |  |  | Weekdays | Grab
|  | REQUIREMENT |  |  |  | Daily Min. |  | Daily Max.
Solids, Total Suspended |  | SAMPLE | ***** | ***** | ***** | ***** | 304.5333 | 1060 | (19) | 0 | THREE/ | Composite
00530 | G 0 0 | MEASUREMENT | [6 empty] | mg/l |  | WEEK
Raw Sew/Influent |  | PERMIT | ***** | ***** | ***** | ***** | Report | Report |  |  | THREE/ | Composite
|  | REQUIREMENT |  |  |  |  | Mon. Avg. | Daily Max. |  |  | WEEK
Solids, Total Suspended |  | SAMPLE | 8.5308 | 0 |  | 4.72 | 0 | 10 | (19) | 0 | THREE/ | Composite
00530 | 1 0 0 | MEASUREMENT |  |  | (26) |  |  |  | mg/l |  | WEEK
Effluent Gross Value |  | PERMIT | 150 | 200 | lbs/day | 30 | 40 | 45 |  |  | THREE/ | Composite
|  | REQUIREMENT | Mon. Avg. | Wkly Avg. |  | Mo Avg. | Wkly Avg. | Daily Max. |  |  | WEEK
Solids, Settleable |  | SAMPLE | ***** | ***** | ***** | ***** | ***** | 0 | (25) | 0 | 5/7 | Composite
00545 | 1 0 0 | MEASUREMENT | [6 empty] | ml/l
Effluent Gross Value |  | PERMIT | ***** | ***** | ***** | ***** | ***** | 1 |  |  | Weekdays | Composite
|  | REQUIREMENT | [5 empty] | Daily Max.
Nitrogen, Ammonia Total |  | SAMPLE | 2.0325 | 0 |  | 1.0656 | 0 | 3.2 | (19) | 0 | THREE/ | Composite
(As N) |  | MEASUREMENT |  |  | (26) |  |  |  | mg/l |  | WEEK
00610 | 1 S 0 | PERMIT | 9.5 | 14 | lbs/day | 1.9 | 2.85 | 3.8 |  |  | THREE/ | Composite
Effluent Gross Value |  | REQUIREMENT | Mon. Avg. | Wkly Avg. |  | Mo Avg. | Wkly Avg. | Daily Max. |  |  | WEEK
Coliform, Fecal MF |  | SAMPLE | ***** | ***** | ***** | ***** | 0 | 0 | (13) | 0 | THREE/ | Grab
M-FC Broth, 44.5C |  | MEASUREMENT | [8 empty] | WEEK
31616 | 1 0 0 | PERMIT | ***** | ***** | ***** | ***** | 200 | 1000 | # / |  | THREE/ | Grab
Effluent Gross Value |  | REQUIREMENT |  |  |  |  | MO GEOMN | Daily Max. | 100 ML |  | WEEK
NAME/TITLE PRINCIPAL EXECUTIVE OFFICER |  |  | I CERTIFY UNDER PENALTY OF LAW THAT I HAVE PERSONALLY EXAMED AND AM FAMILIAR WITH THE INFORMATION |  |  |  |  | TELEPHONE |  |  | DATE
Michael Payne - Utility Director |  |  | SUBMITTED HEREIN; AND BASED ON MY INQUIRY OF THOSE INDIVIDUALS IMMEDIATELY RESPONSIBLE FOR OBTAINING
THE INFORMATION. I BELIEVE THE SUBMITTED INFORMATION IS TRUE. ACCURATE AND CompositeLETE. I AM AWARE
THAT THERE ARE SIGNIFICANT PENALTIES FOR SUBMITTING FALSE INFORMATION. INCLUDING THE POSSIBILITY
|  |  | OF FINE AND IMPRISONMENT SEE 18 U.S.C. & 1001 AND 33 USC & 1319. (PENALTIES UNDER THESE STATUTES MAY |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE |  | 865 | 992-3821
| TYPED OR PRINTED |  | INCLUDE FINES UP TO $10,000 AND OR Max.IMUM IMPRISONMENT OF BETWEEN 6 MONTHS AND 5 YEARS) |  |  | OFFICER OR AUTHORIZED AGENT |  | AREA CODE | NUMBER |  | YEAR MO | DAY
BYPASSING IS ANY DIVERSION OF THE WASTEWATER TREATMENT FACILITY AND FOR OVERFLOWS OF THE COLLECTION
SYSTEM: T = WET WEATHER OCCURANCES AND U = ALL OTHER OCCURANCES
EPA Form 3320-1 (Rev. 9-88) Previous editions may be used. |  |  |  |  | (REPLACES EPA FORM T-40 WHICH MAY NOT BE USED.) |  |  |  |  | Page | 1 | of 3
PERMITTEE NAME/ADDRESS (Include |  |  |  | NATIONAL POLLUTANT DISCHARGE ELIMINATION SYSTEM (NPDES)
Facility Name/Location if different) |  |  |  |  | DISCHARGE MONITORING REPORT (DMR) |  |  |  |  | Form Approved
Name | Maynardville WWTP |  |  | (2-16) |  |  | (17-19) | Minor |  | OMB | No. | 2040-004
Address | P.O. Box 217 |  |  | TN0022870 |  |  | 001 G | Design Capacity of .6 MGD
| Maynardville, TN 37807 |  |  | PERMIT NUMBER |  |  | DISCHARGE NUMBER | (SUBR 03)
| 0 | [6 empty] | F - Final
Facility | Maynardville STP |  |  |  | MONITORING PERIOD |  |  | Design Capacity of .6 MGD
Location | Maynardville, TN 37807 |  |  | FROM YEAR MO | DAY | TO YEAR MO | DAY
|  |  |  | 0 | 1 | 0 | 0 | *** No Discharge |  | ***
Michael Payne - Utility Director |  |  |  | (20-21) (22-23) | (24-25) | (26-27) (28-29) | (30-31) | Note: Read Instructions Before Completing this form.
|  |  | (3 Card Only) QUANTITY OR LOADING |  |  | (4 Card Only) | QUALITY OR CONCENTRATION |  |  | NO. | FREQUENCY | SAMPLE
PARAMETER |  |  | (46-53) | (54-61) |  | (38-45) | (46-53) | (54-61) |  | EX | OF ANALYSIS | TYPE
| (32-37) |  | AVERAGE | MAXIMUM | UNITS | MINIMUM | AVERAGE | MAXIMUM | UNITS | (62-63) | (64-68) | (69-70)
E.COLI, MTEC-MF |  | SAMPLE | ***** | ***** | ***** | ***** | 1.5875 | ***** | ***** | 0 | THREE/ | Grab
|  | MEASUREMENT | [8 empty] | WEEK
31648 | 1 0 0 | PERMIT | ***** | ***** | ***** | ***** | 126 | ***** |  |  | THREE/ | Grab
Effluent Gross Value |  | REQUIREMENT |  |  |  |  | Mo Avg. |  |  |  | WEEK
Flow, In Conduit or thru Treatment |  | SAMPLE | 0.22643 | 0.43 | (03) | ***** | ***** | ***** | ***** | 0 | Daily | Continuous
Plant |  | MEASUREMENT |  |  | MGD
50050 | G 0 0 | PERMIT | Report | Report |  | ***** | ***** | ***** |  |  | Daily | Continuous
Raw Sew/Influent |  | REQUIREMENT | Mon. Avg. | Daily Max.
Flow, In Conduit or thru Treatment |  | SAMPLE | 0.2279 | 0.372 | (03) | ***** | ***** | ***** | (19) | 0 | Daily | Continuous
Plant |  | MEASUREMENT |  |  | MGD |  |  |  | mg/l
50050 | 1 0 0 | PERMIT | Report | Report | ***** | ***** | ***** | ***** |  |  | Daily | Continuous
Effluent Gross Value |  | REQUIREMENT | Mon. Avg. | Daily Max.
Chlorine, Total |  | SAMPLE | ***** | ***** | ***** | ***** | ***** | 0.02 | ***** | 0 | 5/7 | Grab
Residual |  | MEASUREMENT
50060 | 1 0 0 | PERMIT | ***** | ***** | ***** | ***** | ***** | 0.03 |  |  | Weekdays | Grab
Effluent Gross Value |  | REQUIREMENT | [5 empty] | INST. MAX
Overflow Use, |  | SAMPLE | ***** | 0 | (93) | ***** | ***** | ***** | ***** | 0 | Contin | Occurs
Occurances |  | MEASUREMENT |  |  | Occur/ | [5 empty] | uous
74062 | T 0 0 | PERMIT | ***** | Report | Month | ***** | ***** | ***** |  |  | Cont | Occurs
See Comments Below |  | REQUIREMENT |  | Mon. Total | [6 empty] | uous
Overflow Use, |  | SAMPLE | ***** | 0 | (93) | ***** | ***** | ***** | ***** | 0 | Contin | Occurs
Occurances |  | MEASUREMENT |  |  | Occur/ | [5 empty] | uous
74062 | U 0 0 | PERMIT | ***** | Report | Month | ***** | ***** | ***** |  |  | Cont | Occurs
See Comments Below |  | REQUIREMENT |  | Mon. Total | [6 empty] | uous
Bod, Carbonaceous |  | SAMPLE |  |  | ***** | ***** | 278.424 | 356.5 | (19) | 0 | THREE/ | Composite
05 Day, 20C |  | MEASUREMENT | [6 empty] | mg/l |  | WEEK
80082 | G 0 0 | PERMIT |  |  | ***** | ***** | Report | Report |  |  | THREE/ | Composite
Raw Sew/Influent |  | REQUIREMENT |  |  |  |  | Mon. Avg. | DAILY MX |  |  | WEEK
NAME/TITLE PRINCIPAL EXECUTIVE OFFICER |  |  | I CERTIFY UNDER PENALTY OF LAW THAT I HAVE PERSONALLY EXAMin.ED AND AM FAMILIAR WITH THE INFORMATION |  |  |  |  | TELEPHONE |  |  | DATE
Michael Payne - Utility Director |  |  | SUBMITTED HEREIN; AND BASED ON MY INQUIRY OF THOSE INDIVIDUALS IMMEDIATELY RESPONSIBLE FOR OBTAINING
THE INFORMATION. I BELIEVE THE SUBMITTED INFORMATION IS TRUE. ACCURATE AND CompositeLETE. I AM AWARE
THAT THERE ARE SIGNIFICANT PENALTIES FOR SUBMITTING FALSE INFORMATION. INCLUDING THE POSSIBILITY
|  |  | OF FINE AND IMPRISONMENT SEE 18 U.S.C. & 1001 AND 33 USC & 1319. (PENALTIES UNDER THESE STATUTES MAY |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE |  | 865 | 992-3821 |  | 0 | 0
| TYPED OR PRINTED |  | INCLUDE FINES UP TO $10,000 AND OR Max.IMUM IMPRISONMENT OF BETWEEN 6 MONTHS AND 5 YEARS) |  |  | OFFICER OR AUTHORIZED AGENT |  | AREA CODE | NUMBER |  | YEAR MO | DAY
BYPASSING IS ANY DIVERSION OF THE WASTEWATER TREATMENT FACILITY AND FOR OVERFLOWS OF THE COLLECTION
SYSTEM: T = WET WEATHER OCCURANCES AND U = ALL OTHER OCCURANCES
EPA Form 3320-1 (Rev. 9-88) Previous editions may be used. |  |  |  |  | (REPLACES EPA FORM T-40 WHICH MAY NOT BE USED.) |  |  |  |  | Page | 2 | of 3
PERMITTEE NAME/ADDRESS (Include |  |  |  | NATIONAL POLLUTANT DISCHARGE ELIMINATION SYSTEM (NPDES)
Facility Name/Location if different) |  |  |  |  | DISCHARGE MONITORING REPORT (DMR) |  |  |  |  | Form Approved
Name | Maynardville WWTP |  |  | (2-16) |  |  | (17-19) | Minor |  | OMB | No. | 2040-004
Address | P.O. Box 217 |  |  | TN0022870 |  |  | 001 G | Design Capacity of .6 MGD
| Maynardville, TN 37807 |  |  | PERMIT NUMBER |  |  | DISCHARGE NUMBER | (SUBR 03)
| 0 | [6 empty] | F - Final
Facility | Maynardville STP |  |  |  | MONITORING PERIOD |  |  | Design Capacity of .6 MGD
Location | Maynardville, TN 37807 |  |  | FROM YEAR MO | DAY | TO YEAR MO | DAY
|  |  |  | 0 | 1 | 0 | 0 | *** No Discharge |  | ***
Michael Payne - Utility Director |  |  |  | (20-21) (22-23) | (24-25) | (26-27) (28-29) | (30-31) | Note: Read Instructions Before Completing this form.
|  |  | (3 Card Only) QUANTITY OR LOADING |  |  | (4 Card Only) | QUALITY OR CONCENTRATION |  |  | NO. | FREQUENCY | SAMPLE
PARAMETER |  |  | (46-53) | (54-61) |  | (38-45) | (46-53) | (54-61) |  | EX | OF ANALYSIS | TYPE
| (32-37) |  | AVERAGE | MAXIMUM | UNITS | MINIMUM | AVERAGE | MAXIMUM | UNITS | (62-63) | (64-68) | (69-70)
Bod, Carbonaceous |  | SAMPLE | 8.7021 | 0 |  | 4.85 | 0 | 6.6 | (19) | 0 | THREE/ | Composite
05 Day, 20C |  | MEASUREMENT |  |  | (26) | [5 empty] | WEEK
80082 | G 0 0 | PERMIT | 125 | 175 | lbs/day | 25 | 35 | 40 |  |  | THREE/ | Composite
EFFLUENT GROSS VALUE |  | REQUIREMENT | Mon. Avg. | Wkly Avg. |  | Mo Avg. | Wkly Avg. | Daily Max. | MG/L |  | WEEK
Bypass of Treatment |  | SAMPLE | ***** | 0 | ***** | ***** | ***** | ***** | ***** | 0 | Contin | Occurs
80998 | T 0 0 | MEASUREMENT | [8 empty] | uous
See Comments Below |  | PERMIT | ***** | Report | ***** | ***** | ***** | ***** |  |  | Cont | Occurs
|  | REQUIREMENT |  | Mon. Total | [6 empty] | uous
Solids, Suspended |  | SAMPLE | ***** | ***** | ***** | 96.18% | 98.06% | ***** | (23) | 0 | THREE/ | Calculated
Percent Removal |  | MEASUREMENT | [6 empty] | Percent |  | WEEK
81011 | K 0 0 | PERMIT | ***** | ***** | ***** | 40% | 85% | ***** |  |  | THREE/ | Calculated
Percent Removal |  | REQUIREMENT |  |  |  | Min. % Rmv | Mon. Av. Min. |  |  |  | WEEK
Carbonanceous Oxygen Demand |  | SAMPLE |  |  |  | 95.6% | 98.12% | ***** | (23) | 0 | THREE/ | Calculated
% Removal |  | MEASUREMENT | [6 empty] | Percent |  | WEEK
81363 | K 0 0 | PERMIT |  |  |  | 40% | 85% | ***** |  |  | THREE/ | Calculated
Percent Removal |  | REQUIREMENT |  |  |  | Min. % Rmv | Mon. Av. Min. |  |  |  | WEEK
SAMPLE
MEASUREMENT
PERMIT
REQUIREMENT
SAMPLE
MEASUREMENT
PERMIT
REQUIREMENT
SAMPLE
MEASUREMENT
PERMIT
REQUIREMENT
NAME/TITLE PRINCIPAL EXECUTIVE OFFICER |  |  | I CERTIFY UNDER PENALTY OF LAW THAT I HAVE PERSONALLY EXAMin.ED AND AM FAMILIAR WITH THE INFORMATION |  |  |  |  | TELEPHONE |  |  | DATE
Michael Payne - Utility Director |  |  | SUBMITTED HEREIN; AND BASED ON MY INQUIRY OF THOSE INDIVIDUALS IMMEDIATELY RESPONSIBLE FOR OBTAINING
THE INFORMATION. I BELIEVE THE SUBMITTED INFORMATION IS TRUE. ACCURATE AND CompositeLETE. I AM AWARE
THAT THERE ARE SIGNIFICANT PENALTIES FOR SUBMITTING FALSE INFORMATION. INCLUDING THE POSSIBILITY
|  |  | OF FINE AND IMPRISONMENT SEE 18 U.S.C. & 1001 AND 33 USC & 1319. (PENALTIES UNDER THESE STATUTES MAY |  |  | SIGNATURE OF PRINCIPAL EXECUTIVE |  | 865 | 992-3821 |  | 0 | 0
| TYPED OR PRINTED |  | INCLUDE FINES UP TO $10,000 AND OR Max.IMUM IMPRISONMENT OF BETWEEN 6 MONTHS AND 5 YEARS) |  |  | OFFICER OR AUTHORIZED AGENT |  | AREA CODE | NUMBER |  | YEAR MO | DAY
BYPASSING IS ANY DIVERSION OF THE WASTEWATER TREATMENT FACILITY AND FOR OVERFLOWS OF THE COLLECTION
SYSTEM: T = WET WEATHER OCCURANCES AND U = ALL OTHER OCCURANCES
EPA Form 3320-1 (Rev. 9-88) Previous editions may be used. |  |  |  |  | (REPLACES EPA FORM T-40 WHICH MAY NOT BE USED.) |  |  |  |  | Page | 3 | of 3
Formulas:
TO YEAR MO = +[TN0022870]

## DMRVIO
DMR Violation Calculations
2024-04-01
| BOD | TSS | SET S | D.O. | pH | Nh3-N | E-Coli | Fecal | Chlorine
Daily Limiit | 40 | 45 | 1 | 5 | 6 to 9 | 3.8 |  | 1000 | 0.03
Exceedances | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Mo Avg (mg/l) | 25 | 30 |  |  |  | 1.9 | 126 | 200
Exceedances | 0 | 0 |  |  |  | 0 | 0 | 0
Wkly Avg (mg/l) | 35 | 40 |  |  |  | 2.85
Exceedances | 0 | 0 |  |  |  | 0
Mo Avg (lbs) | 125 | 150 |  |  |  | 9.5
Exceedances | 0 | 0 |  |  |  | 0
Wkly Avg (lbs) | 175 | 200 |  |  |  | 14
Exceedances | 0 | 0 |  |  |  | 0 | 0 | 0
Percent Removal
Min | 40% | 40%
Exceedances | 0 | 0
Avg | 85% | 85%
Exceedances | 0 | 0
Overflow Viloations | Totals
Wet Wearther | 0
Other Overflows | 0
DMR Reporting Month
| From |  |  | To
| Year | Month | Day | Year | Month | Day
Change Brown Numbers Only |  |  | 1 | 0

## Graphs
Permit Maximum is Red Line @ 0.03 mg/l.

## Sludge Disp.
City of Maynardville WWTP
Sludge Application Activities
Month of : |  | 2024-04-01
Date | [9 empty] | Comments
1
2 | Shipped | 10.74 | tons | to the | Chestnut | Ridge | Landfill in | Heiskell, | TN. | 10.74 tons shipped.
3
4
5 | Shipped | 10.79 | tons | to the | Chestnut | Ridge | Landfill in | Heiskell, | TN. | 10.79 tons shipped.
6
7
8
9 | Shipped | 12.32 | tons | to the | Chestnut | Ridge | Landfill in | Heiskell, | TN. | 12.32 tons shipped.
10
11
12
13
14
15 | Shipped | 8.17 | tons | to the | Chestnut | Ridge | Landfill in | Heiskell, | TN. | 8.17 tons shipped.
16
17
18
19
20
21
22
23 | Shipped | 9.75 | tons | to the | Chestnut | Ridge | Landfill in | Heiskell, | TN. | 9.75 tons shipped.
24
25 | Shipped | 8.31 | tons | to the | Chestnut | Ridge | Landfill in | Heiskell, | TN. | 8.31 tons shipped.
26
27
28
29
30 | Shipped | 9.9 | tons | to the | Chestnut | Ridge | Landfill in | Heiskell, | TN. | 9.90 tons shipped.
Total

## Overflows
City of Maynardville
Collection Overflow Report
2024-04-01
Total Wet Weather Overflows |  |  | 0 | Total Other Overflows |  |  | 0
Overflow | Over Flow | Over Flow | Over Flow |  | Type | Reported | Reported | Reported | Reported
Number | Date | Time | Location |  | W or O | Date | Time | To | By | Comments
Zero | Overflows | for | April 2024.

## printlab
Maynardville Wastewater Treatment Plant | [10 empty] | Plant Inf. TSS | 0
Laboratory Record of Analysis | [10 empty] | Aer Inf. TSS | 0
24-Hour Composite Samples | [5 empty] | Receiving Stream |  |  |  |  | Filter Inf. TSS | 0
Time taken to Lab from Sampler: | [5 empty] | Date | 0 |  |  |  | Final Eff. TSS | 0
Operator Transporting Sample to Lab | [5 empty] | Time of Sample |  |  |  |  | AERATION MLSS | 0
Date Collected: | [5 empty] | Time to Lab |  |  |  |  | Stream Above TSS | 0
Date of Analysis: | [5 empty] | Collected by |  |  |  |  | Stream Below TSS | 0
Lab Tech Perforing Test: | [5 empty] | Sample Type |  |  |  |  | CRIP INF TSS | 0
Collection Temp. (c): | [10 empty] | CRIP EFF TSS | 0
Influent |  | Effluent | [8 empty] | CRIP MLSS | 0
[11 empty] | Plant Inf. Sets | 0
Suspended Solids (SM 209D/EPA M 160.2)
[7 empty] | Grab Sample Time |  |  |  | Aer Inf. Set S. | 0
[11 empty] | Filter Inf. Set S. | 0
Main Plant | [6 empty] | Receiving Stream |  |  |  | Final Eff. Set S. | 0
| Plant Inf. | Plant Effluent | Aer 1 MLSS | Aer 2 MLSS | RAS | Digestor | Stream Above | Stream Below |  |  | Other Set S. | 0
Filtration Time | [10 empty] | Stream Above Set S. | 0
Filter # | 1 | 2 | 3 | 4 | 5 | 6 | S1 | S2 |  |  | Stream Below Set S. | 0
Amt Filtered (ml) | [10 empty] | CRIP INF Set S. | 0
Filter & Solids Wt | [10 empty] | CRIP EFF Set S. | 0
Filter Wt (paper) | [10 empty] | CRIP MLSS Set S. | 0
Solids | [10 empty] | Plant Inf. Ammonia | 0
Suspended Solids (mg/l) | [10 empty] | Aer Inf. Ammonia | 0
Max Value | [10 empty] | Filter Inf. Ammonia | 0
Settable Solids (SM 213B) | [10 empty] | Other Ammonia | 0
Main Plant | [5 empty] | Receiving Stream |  |  |  |  | Stream Above Ammonia | 0
| Plant Inf. | Plant Effluent | Aeration 1 | Aeration 2 | Other | Stream Above | Stream Below |  |  |  | Stream Below Ammonia | 0
Pour Time | [10 empty] | CRIP INF Ammonia | 0
Read Time | [10 empty] | CRIP EFF Ammonia | 0
Settable Solids (ml/l) | [10 empty] | CRIP Other Ammonia | 0
Max Value | [10 empty] | Plant Inf. pH | 0
[11 empty] | Aer Inf. pH | 0
Ammonia Nitrogen (SM 417E) | [10 empty] | Filter Inf. pH | 0
Main Plant | [5 empty] | Receiving Stream |  |  |  |  | Final Eff. pH | 0
| Plant Inf. | Plant Effluent | Aeration 1 | Aeration 2 | Other | Stream Above | Stream Below |  |  |  | Other pH | 0
Analysis Time | [10 empty] | Stream Above pH | 0
Ammonia N (mg/l) | [10 empty] | Stream Below pH | 0
Max Value | [10 empty] | CRIP INF pH | 0
[11 empty] | CRIP EFF pH | 0
pH Determination (SM 423) | [10 empty] | CRIP Other pH | 0
Main Plant | [5 empty] | Receiving Stream |  |  |  |  | Plant Inf. BOD | 0
| Plant Inf. | Plant Effluent | Aeration 1 | Aeration 2 | Digestor | Stream Above | Stream Below |  |  |  | Aer Inf. BOD | 0
Analysis Time | [10 empty] | Filter Inf. BOD | 0
pH Units | [10 empty] | Final Eff. BOD | 0
Max Value | [10 empty] | Blank BOD | 0
[11 empty] | Stream Above BOD | 0
Carbonaceous Biochemical Oxygen Demand ( 5 Day) (SM 507/EPA M 405.1) | [8 empty] | BOD- 5 Day Testing |  | Stream Below BOD | 0
Main Plant | [8 empty] | Receiving Stream |  | CRIP INF BOD | 0
| Seeded Blank | Blank 1 | Blank 2 | Influent | Influent | Effluent | Effluent | Effluent | Stream Above | Stream Below | CRIP EFF BOD | 0
Analysis Time: | [10 empty] | CRIP Blank BOD | 0
Sample Size (ml or %) | [10 empty] | Plant Inf. DO | 0
Bottle # | [10 empty] | Aer Inf. DO | 0
Initial DO | [10 empty] | Filter Inf. DO | 0
Read Date | [10 empty] | Final Eff. DO | 0
Final DO | [10 empty] | Other DO | 0
Oxygen Demand | [10 empty] | Stream Above DO | 0
Blank Correction
Dilution Factor | [10 empty] | Stream Below DO | 0
( C ) BOD5 (mg/l) | [10 empty] | Crip Influent DO | 0
Average | [10 empty] | Crip Effluent DO | 0
Max Value | [10 empty] | Crip Other DO | 0
[11 empty] | Plant Inf. Temp. | 0
Dissolved Oxygen (SM 421F) and Temperature & Total Chlorine Reidual | [10 empty] | Aer Inf. Temp. | 0
Main Plant | [5 empty] | Receiving Stream |  |  |  |  | Filter Inf. Temp. | 0
| Plant Inf. | Plant Effluent | Aeration 1 | Aeration 2 | Digestor | Stream Above | Stream Below |  |  |  | Final Eff. Temp. | 0
Analysis Time | [10 empty] | Other Temp. | 0
Dissolved Oxygen | [10 empty] | Stream Above Temp. | 0
Min Value | [10 empty] | Stream Below Temp. | 0
Temp. C | [10 empty] | Crip Influent Temp. | 0
Chlorine Residual | Before SO2 |  | After SO 2 | [7 empty] | Crip Effluent Temp. | 0
| Calibrations Performed | [9 empty] | Crip Other Temp. | 0
| Date | Item | Method
D.O. Probe
BOD Probe
Comments: |  | Ammonia Probe
pH Probe
Bacteriological Worksheet Method: Hach MFC Filter Broth - Fecal Coliform
| Control Blank | Plant Effluent |  |  | Stream Ablove |  |  | Stream Below
Collection Date
Collection Time
Collected By
Date Analyzed
Time Analyzed
Analyzed By
Read Date
Read Time
Read By
Sample #
Volume Filtered
Coliform Count
Coliform per 100 ml
E. Coli MPN
Max Value
Total Solids/Volatile Solids: (S.M. 209A / S.M. 2092)
| Aeration 1 | Aeration 2 | Digestor | Sludge Hauled
Collected By
Time Collected
Analysis Time
Sample Type
Dish wt+Sample
Dish Wt
Sample Wt
Wt After Drying
Wt Dry Solids
Total Solids %
Wt after Burn
Wt Vol Solids
Volatile %
pH Value