## protection crit
Portland WWTP
Initial | 9.3.2021 |  |  | POTW Capacity = 1.9 MGD, Current Flow = 1.8 MGD, Nitrification required, Local Limits allocated for equal distribution of remaining 0.114 MGD
Plant Protection Limits
|  | Pass through, 11.26.19 | Activated Sl. |  |  |  | Inhibition Con. ug/L |  |  | Biosolids | 503
Parameter |  | Con. ug/L | % removal | Plant Protection ug/L | Source | Process |  |  |  | Criteria ug/L | Ceil. cont | % solids | MGD Sludge | MGD Cap
|  | C | D | E |  |  |  | I |  | K | L | M | N | O
|  |  |  | C/(1-(D/100)) | [5 empty] | 8.34*L*M*N/(D/100)/(8.34*1.9)*1000
CBOD May-Oct |  | 10500 | 97 | 350000
CBOD N-April |  | 15700 | 97 | 523333.3333
TSS |  | 30000 | 98 | 1500000
Ammonia M-Oct |  | 1100 | 98 | 55000 |  |  |  | 480000
Ammonia N-April |  | 2200 | 98 | 110000 |  |  |  | 480000
Arsenic |  |  | 45 |  | TN Guidance | Activated Sludge |  | 100 |  | 18.4211 | 75 | 0.012 | 0.0175 | 1.8
Copper* (84) |  | 30.17 | 88 | 251.4167 | EPA | 50% Nitrification |  | 265 |  | 540.0718 | 4300 | 0.012 | 0.0175 | 1.8
Chromium III |  |  |  |  | EPA | Nitrification |  | 250
Chromium VI |  | 10.08 | 84 |  | EPA | Nitrification |  | 250
Chromium |  |  | 84 | 0 | EPA | Nitrification |  | 250
Nickel* (34) |  | 143.02 | 43 | 250.9123 | EPA | Nitrification |  | 250 |  | 107.9559 | 420 | 0.012 | 0.0175 | 1.8
Cadmium |  | 1.11 | 85 | 7.4 | TN Guidance | Nitrification |  | 1000 |  | 11.0526 | 85 | 0.012 | 0.0175 | 1.8
Lead |  | 17.5 | 82 | 97.2222 | TN Guidance | Activated Sludge |  | 100 |  | 113.2221 | 840 | 0.012 | 0.0175 | 1.8
Mercury* (76) |  | 0.05 | 96 | 1.25 | TN Guidance | Activated Sludge |  | 100 |  | 6.5625 | 57 | 0.012 | 0.0175 | 1.8
Zinc* (81) |  | 200 | 58 | 476.1905 | EPA | 50% Nitrification |  | 290 |  | 1429.2196 | 7500 | 0.012 | 0.0175 | 1.8
Molybdenum |  |  | 41 | [6 empty] | 20.2182 | 75 | 0.012 | 0.0175 | 1.8
Selenium |  |  | 73 | [6 empty] | 15.1406 | 100 | 0.012 | 0.0175 | 1.8
Silver, daily max. |  | 5 | 83 | 29.4118 | TN Guidance | Activated Sludge |  | 250
Cyanide |  | 4.77 | 62 | 12.5526 | TN Guidance | Activated Sludge |  | 100
Toluene |  | 15 | 93 | 214.2857 | TN Guidance | Activated Sludge |  | 200000
Benzene |  | 3 | 77 | 13.0435 | TN Guidance | Activated Sludge |  | 100000
1,1,1-Trichloroethane |  | 30 | 88 | 250
Ethybenzene |  | 4 | 90 | 40 | TN Guidance | Activated Sludge |  | 200000
Carbon Tetrachloride |  | 15 | 99 | 1500
Chloroform |  | 85 | 62 | 223.6842 | EPA | Nitrification |  | 10000
Tetrachloroethylene |  | 25 | 82 | 138.8889
Trichlorethylene |  | 10 | 90 | 100
1,2 Transdichloroethylene |  | 1.5 | 80 | 7.5
Methylene chloride |  | 50 | 48 | 96.1538
Phenol |  | 50 | 83 | 294.1176 | EPA | Nitrification |  | 4000
Naphthalene |  | 1 | 92 | 12.5 | EPA | Activated Sludge |  | 500000
Bis(2-ethyl hexyl) phathalate |  |  | 62 | 0
Butyl benzyl phathalate |  |  | 94 | 0
Di-n-butyl phathalate |  |  | 68 | 0
Diethyl phathalate |  |  | 91 | 0
Total Phathalate |  | 64.5 | 62 | 169.7368
* Actual percent removal, book value added
| B |  | D |  |  |  |  | J | K | L |  | N |  | P | S
Pollutant Loading |  |  | MAHL | [10 empty] | MAIL
[14 empty] | Reseve Percent "Zero" | Local Limit Monthly Average
Parameter | Plant Protection Criteria ug/L |  | Loading lbs/day @ 1.9 MG Flow |  |  |  |  | Residential Loading |  |  |  | Available Loading |  |  | "@ .114MGD
| B= lowest value of column |  | B/1000*8.34*1.9 |  |  |  |  | mg/l | Flow | Load in lbs | [6 empty] | Daily Max
| 'E,I,K | [8 empty] | I*J*8.34 |  | D-L= lbs |  |  | P/8.34*.114
Arsenic | 18.421 |  | 0.2919 |  |  |  |  | 0.0275 | 1.786 | 0.40962 |  | -0.11772 |  | -0.11772 | -0.12382 | Arsenic
Copper | 251.42 |  | 3.984 |  |  |  |  | 0.0577 | 1.786 | 0.85946 |  | 3.1245 |  | 3.1245 | 3.2864 | Copper | 4.9295
Chromium III | 250 |  | 3.9615 |  |  |  |  | 0.0055 | 1.786 | 0.081924 |  | 3.8796 |  | 3.8796 | 4.0805 | Chromium III | 6.1207
Chromium VI | 250 |  | 3.9615 |  |  |  |  | 0.032 | 1.786 | 0.47665 |  | 3.4849 |  | 3.4849 | 3.6653 | Chromium VI | 5.498
Chromium | 250 |  | 3.9615 |  |  |  |  | 0.00563 | 1.786 | 0.08386 |  | 3.8776 |  | 3.8776 | 4.0785 | Chromium | 6.1177
Nickel | 107.9559 |  | 1.7107 |  |  |  |  | 0.0154 | 1.786 | 0.22939 |  | 1.4813 |  | 1.4813 | 1.558 | Nickel | 2.337
Cadmium | 7.4 |  | 0.11726 |  |  |  |  | 0.0005 | 1.786 | 0.0074476 |  | 0.10981 |  | 0.10981 | 0.1155 | Cadmium | 0.17325
Lead | 97.22 |  | 1.5405 |  |  |  |  | 0.0001 | 1.786 | 0.0014895 |  | 1.5391 |  | 1.5391 | 1.6188 | Lead | 2.4281
Mercury | 1.25 |  | 0.019807 |  |  |  |  | 8.8575e-06 | 1.786 | 0.00013193 |  | 0.019676 |  | 0.019676 | 0.020695 | Mercury | 0.031042
Zinc | 290 |  | 4.5953 |  |  |  |  | 0.104 | 1.786 | 1.5491 |  | 3.0462 |  | 3.0462 | 3.204 | Zinc | 4.806
Molybdenum | 20.218 |  | 0.32037 |  |  |  |  | 0.0066 | 1.786 | 0.098309 |  | 0.22207 |  | 0.22207 | 0.23357 | Molybdenum | 0.35035
Selenium | 15.14 |  | 0.23991 |  |  |  |  | 0.0004 | 1.786 | 0.0059581 |  | 0.23395 |  | 0.23395 | 0.24607 | Selenium | 0.3691
Silver, Daily Maximum | 29.41 |  | 0.46603 |  |  |  |  | 0.0005 | 1.786 | 0.0074476 |  | 0.45858 |  | 0.45858 |  | Silver | 0.48233
Cyanide | 12.63 |  | 0.20013 |  |  |  |  | 0.0025 | 1.786 | 0.037238 |  | 0.1629 |  | 0.1629 | 0.17133 | Cyanide | 0.257
Toluene | 214.29 |  | 3.3956 |  |  |  |  | 0.0049 | 1.786 | 0.072987 |  | 3.3227 |  | 3.3227 | 3.4947 | Toluene | 5.2421
Benzene | 13.04 |  | 0.20663 |  |  |  |  | 0.0031 | 1.786 | 0.046175 |  | 0.16046 |  | 0.16046 | 0.16877 | Benzene | 0.25315
1,1,1-Trichloroethane | 250 |  | 3.9615 |  |  |  |  | 0.0031 | 1.786 | 0.046175 |  | 3.9153 |  | 3.9153 | 4.1181 | 1,1,1-Trichloroethane | 6.1771
Ethybenzene | 40 |  | 0.63384 |  |  |  |  | 0.0031 | 1.786 | 0.046175 |  | 0.58766 |  | 0.58766 | 0.6181 | Ethybenzene | 0.92715
Carbon Tetrachloride | 1500 |  | 23.769 |  |  |  |  | 0.0005 | 1.786 | 0.0074476 |  | 23.7616 |  | 23.7616 | 24.9922 | Carbon Tetrachloride | 37.4882
Chloroform | 223.68 |  | 3.5444 |  |  |  |  | 0.00945 | 1.786 | 0.14076 |  | 3.4037 |  | 3.4037 | 3.58 | Chloroform | 5.3699
Tetrachloroethylene | 138.89 |  | 2.2009 |  |  |  |  | 0.0005 | 1.786 | 0.0074476 |  | 2.1934 |  | 2.1934 | 2.307 | Tetrachloroethylene | 3.4605
Trichlorethylene | 100 |  | 1.5846 |  |  |  |  | 0.001 | 1.786 | 0.014895 |  | 1.5697 |  | 1.5697 | 1.651 | Trichlorethylene | 2.4765
1,2 Transdichloroethylene | 7.5 |  | 0.11884 |  |  |  |  | 0.0005 | 1.786 | 0.0074476 |  | 0.1114 |  | 0.1114 | 0.11717 | 1,2 Transdichloroethylene | 0.17575
Methylene chloride | 96.15 |  | 1.5236 |  |  |  |  | 0.0428 | 1.786 | 0.63752 |  | 0.88608 |  | 0.88608 | 0.93197 | Methylene chloride | 1.3979
Phenol | 294.12 |  | 4.6606 |  |  |  |  | 0.0674 | 1.786 | 1.0039 |  | 3.6567 |  | 3.6567 | 3.8461 | Phenol | 5.7691
Naphthalene | 12.5 |  | 0.19808 |  |  |  |  | 0.0264 | 1.786 | 0.39323 |  | -0.19516 |  | -0.19516 | -0.20527 | Naphthalene
Bis(2-ethyl hexyl) phathalate |  |  | 0 | [6 empty] | 0 |  | 0 |  | 0 |  | Bis(2-ethyl hexyl) phathalate
Butyl benzyl phathalate |  |  | 0 | [6 empty] | 0 |  | 0 |  | 0 |  | Butyl benzyl phathalate
Di-n-butyl phathalate |  |  | 0 | [6 empty] | 0 |  | 0 |  | 0 |  | Di-n-butyl phathalate
Diethyl phathalate |  |  | 0 | [6 empty] | 0 |  | 0 |  | 0 |  | Diethyl phathalate
Total Phathalate | 169.74 |  | 2.6897 |  |  |  |  | 0.121 | 1.786 | 1.8023 |  | 0.88738 |  | 0.88738 | 0.93333 | Total Phathalate | 1.4
0
BOD May-Oct | 350000 |  | 5546.1
BOD Nov-April | 523333 |  | 8292.7347
TSS | 1500000 |  | 23769
Ammonia M-Oct | 55000 |  | 871.53
Ammonia N-April | 110000 |  | 1743.06

## ResidentialCommercial
Residential/Commercial Monitoring
BOLD values detected
| Saul 1 | Saul 2 | Wynwood1 | Wynwood2 | SAUL 1 | WynnWood 2 | 29 TN city summary of detected values
| 6.10.21 | 6.10.21 | 6.10.21 | 6.10.21 | 8.17.21 | 8.17.21
T nitrogen | 83.5 | 84.5 | 81 | 83 | 75 | 71
TKN | 83.5 | 84.5 | 80.6 | 82.5 | 75 | 71
T Phos | 9 | 8.95 | 7.4 | 7.65 | 8.25 | 9.7
TSS | 108 | 119 | 133 | 130
BOD | 273 | 131 | 279 | 285
Chloride | 56 | 56.3 | 51.4 | 52.8 | 54.7 | 58.8
Values To Use
Arsenic | [6 empty] | 0.0275 | 0.0275
Copper | [6 empty] | 0.0577 | 0.0577
Chromium III | [6 empty] | 0.0055 | 0.0055
Chromium VI | [6 empty] | 0.032 | 0.032
Chromium | [6 empty] | 0.00563 | 0.00563
Nickel | [6 empty] | 0.0154 | 0.0154
Cadmium | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |  | 0.0005
Lead | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 |  | 0.0001
Mercury | 9.45e-06 | 9.08e-06 | 8.27e-06 | 8.63e-06 |  |  |  | 8.8575e-06
Zinc | [6 empty] | 0.104 | 0.104
Molybdenum | [6 empty] | 0.0066 | 0.0066
Selenium | [6 empty] | 0.0004 | 0.0004
Silver | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |  | 0.0005
Cyanide | 0.005 | 0.005 |  |  | 0.005 | 0.005 |  | 0.0025
Toluene | [6 empty] | 0.0049 | 0.0049
Benzene | [6 empty] | 0.0031 | 0.0031
1,1,1-Trichloroethane | [6 empty] | 0.0031 | 0.0031
Ethybenzene | [6 empty] | 0.0031 | 0.0031
Carbon Tetrachloride | [6 empty] | 0.001 | 0.0005
Chloroform | [6 empty] | 0.00945 | 0.00945
Tetrachloroethylene | [6 empty] | 0.001 | 0.0005
Trichlorethylene | [6 empty] | 0.001 | 0.001
1,2 Transdichloroethylene | [6 empty] | 0.001 | 0.0005
Methylene chloride | [6 empty] | 0.0428 | 0.0428
Phenol | [6 empty] | 0.0674 | 0.0674
Naphthalene | [6 empty] | 0.0264 | 0.0264
Bis(2-ethyl hexyl) phathalate
Butyl benzyl phathalate
Di-n-butyl phathalate
Diethyl phathalate
Total Phathalate | [6 empty] | 0.121 | 0.121

## Rationale
Plant Status: Permitted capacity 1.9 MGD, average flow = 1.8 MGD, nitrification required, local limits equal allocation across 0.4 MGD of SIU flow
Pass Through Limits from TDEC on 11.26. 2019
Percent Removal reviewed and used actual data from the past three years or book values from the TN Guidance
Inhibition data from either the TN or EPA Guidance and the biomass to protect is noted
Biosolids data are from 2021 removal tonnage
Plant Protection Criteria are chosen from the lowest values in columns E, J, or L and then entered on the lower half of the spreadsheet in Column B
MAHL is located in Column D, lower half of the sheet, and is scaled to full capacity
Residential Commercial Background testing is summarized on a separate sheet of this workbook. This testing has proved to be a major struggle to get the Lab to test for the correct parameters. Four tests in June were incomplete because the lab was requested to do the "old" list. Test in August this same error occurred even though the Coordinator e-mailed the lab the exact list, and by the time the error was detected it was too late to retest. Instead of using EPA 1980 values an averate of 29 Tennessee cities detected values are used. These have been accepted in the past by Laurel and Jennifer.
Residential Commercial flow is scaled to full capacity using the actual percent of R/C flow at the time of calculation
There is no reserve. The plant is at full capacity. No new industrial load can be accepted, but an upgrade and expansion is in beginning.
Local limits are based on 114,000 gpd of industrial flow, no more can be accepted.
Daily Maxuum values are set at 1.5 times monthly average.
There are two negative values in the Local Limit list. We assume a BDL limit, should be used in SIU permits. Better residential/commercial tests should correct this.